## Skaičiuoklė
Į šia spalva pažymėtus langelius reikia įvesti duomenis
Elektros variklių keitimas
Ši skaičiuoklė susijusi su esamų variklių (IE2 efektyvumo klasės arba senesnių) pakeitimu efektyvesnėmis technologijomis (IE3 efektyvumo klasės arba naujesnėmis) nepasibaigus jų eksploatavimo laikui. Pateiktos įgyvendintų priemonių energijos sutaupymo skaičiavimo formulės, kuriose atsižvelgiama ne tik į esamų variklių keitimą, bet ir į kintamo greičio pavarų (VSD) montavimą. Jei esamo variklio pakeitimo į efektyvesnį metu yra sumontuojama kintamo greičio pavara, tuomet vertinamas papildomas energijos sutaupymas TFESVSD. Ši supaprastinta standartizuota skaičiuoklė skirta skaičiuoti Energijos sutaupymo susitarimų energijos sutaupymams.
Įgyvendintos energijos taupymo priemonės duomenys*
Data Input
Conversion factors |  |  | EU values are provided by streamSAVE. If you want to use national values, please fill in the relevant values in the corresponding table in sheet "National values".
Power Range |  |  | Indicative values are available for different nominal power ranges of the new motor. Please choose accordingly.
Effciency of the new motors |  |  | Indicative values are available for different efficiency classes (IE3 or IE4) of new motor. Please choose accordingly.
Sector |  |  | Annual operating hours depend on the sector and activity profile. Please choose accordingly.
Ar prie efektyvesnio el. variklio montuojama kintamo greičio pavara? |  |  | Additional savings can be achieved by the installation of a variable speed drive (VSD). Please choose accordingly.
End-Use (VSD) |  |  | In case a variable speed drive is installed, please coose the relevant end-use.
Share of energy carriers
| before implementation | share | after implementation | share | Parameter explanation
Input energy of appliance before and after implementing the energy-saving action
Input energy of appliance before and after implementing the energy-saving action
Input energy of appliance before and after implementing the energy-saving action
Input energy of appliance before and after implementing the energy-saving action
Input energy of appliance before and after implementing the energy-saving action
| total share | 0% | total share | 0% | Checksum for the total share of energy carriers
| fPE, before | 0 | fPE, after | 0 | Factor for converting final energy consumption into primary energy consumption
| fGHG, before | 0 | fGHG, after | 0 | Factor for converting energy consumption into greenhouse gas emissions
Papildomo energijos sutaupymo faktorius dėl sumontuotos variklio kintamo greičio pavaros
| Faktiniai įvesties duomenys | Matavimo vienetai | Indicative Values | Unit | Dydžio paaiškinimas | Rekomenduojamas duomenų šaltinis** | Galutinis vartotojas | fVSD
n |  | vnt. |  | dmnl | Pakeistų variklių skaičius | Faktiniai duomenys iš techninės dokumentacijos | Siurblys | 0.28
Pn |  | kW |  | kW | Vardinė (nominali) varikio galia | Pagal įrenginio technines charakteristikas | Ventiliatorius | 0.28
h |  | h | - | h | Metinės darbo (veikimo) valandos | Faktinis įrenginio veikimo laikas, gali būti fiksuojamas įmonės dokumentuose | Oro kompresorius | 0.12
Ƞc |  | % | - | % | Pakeisto variklio efektyvumo koeficientas | Pagal įrenginio technines charakteristikas | Aušinimo kompresorius | 0.12
Ƞhe |  | % | - | % | Efektyvesnio variklio efektyvumo koeficientas | Pagal įrenginio technines charakteristikas | Konvejeriai | 0.12
LF |  | - | 0.6 | dmnl | Apkrovos koeficientas | Įmonės faktiniai duomenys. Neturint konkrečių duomenų galima naudoti 0,6 reikšmę | Kiti varikliai | 0.12
fVSD |  | - | - | dmnl | Papildomo energijos sutaupymo faktorius dėl sumontuotos variklio kintamo greičio pavaros | Dydis imamas iš šalia pateiktos lentelės
Skaičiavimo formulė*
Bendras galutinės energijos sutaupymas (TFES) |  |  |  |  | Papildomas energijos sutaupymas, jei montuojama kintamo greičio pavara:
Article 3 ¦ Total final energy savings (TFES)
Article 3 ¦ Effect on primary energy consumption (EPEC)
GHG ¦ Greenhouse gas savings (GHGsav)
Rezultatai*
| Sutaupyta energija | Matavimo vienetai | indicative calculation values | Unit | Dydžio paaiškinimas
| Nepakanka duomenų | kWh/metus | insufficient data | kWh/a | Bendras galutinės energijos sutaupymas
EFE Article 3 | insufficient data | kWh/a | insufficient data | kWh/a | Effect on the final consumption for Article 3 calculation
TPES Article 3 | insufficient data | kWh/a | insufficient data | kWh/a | Total primary energy savings for Article 3 calculation
GHGsav | insufficient data | tCO2 | insufficient data | tCO2 | Greenhouse gas savings
Costs related to the action
| [euro2021] |  | Investment costs |  | Parameter explanation
|  |  | IE3 | IE4
| [0,75 kW - 7,5 kW] |  | 188 | 244 | Average cost for that power range, Including motor purchase and installation Costs
| [7,5 kW - 75 kW] |  | 720 | 900
| [75 kW - 375 kW] |  | 6900 | 8280
| [375 kW - 1000 kW] |  | 28750 | 34500
| [euro2021/a] |  | Variable operational cost
| Energy costs |  | Energy use*electricity price |  | Energy costs
| [euro2021/a] |  | Fixed operational costs
| [75 kW - 375 kW] |  | 6000 |  | Maintenance costs, including rewindings over product lifetime
| [375 kW - 1000 kW] |  | 20000
| [a] |  | LifetimePA
| Lifetime |  | 10 |  | Lifetime of the equipment
* - Parengta pagal tarptautinio projekto streamSAVE įgyvendinimo metu sukurtą metodiką.
** - Pateikiamas rekomenduojamas, o ne privalomas duomenų šaltinis.

## EU Values (hidden)
Conversion factors
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-]
Electricity | 133.3 | 2.2813
District heat | 209.9 | 1.6631
Natural gas | 201.96 | 1.007
Gas/Diesel oil | 266.76 | 1.1187
Motor gasoline | 249.48 | 1.1187
Biodiesels | 0 | 1.0008
Biogasoline | 0 | 1.0008
Other liquid biofuels | 0 | 1.0008
Biogas | 0 | 1.0321
Wood/wood waste | 0 | 1.0008
Other primary solid biomass | 0 | 1.0008
Kerosene (other than jet kerosene) | 258.84 | 1.1187
Liquefied petroleum gases | 227.16 | 1.1187
Naphtha | 263.88 | 1.1187
Natural gas liquids | 231.12 | 1.1187
Petroleum coke | 351 | 1.1187
Refinery gas | 207.36 | 1.1187
Residual fuel oil | 278.64 | 1.1187
White spirit and SBP | 263.88 | 1.1187
Other petroleum products | 263.88 | 1.1187
Anthracite | 353.88 | 1.0024
Lignite | 363.6 | 1.0024
Charcoal | 0 | 1.0008
Coal tar | 290.52 | 1.0024
Coke oven coke and lignite coke | 385.2 | 1.0024
Coking coal | 340.56 | 1.0024
Patent fuel | 351 | 1.0024
Sub-bituminous coal | 345.96 | 1.0024
Other bituminous coal | 340.56 | 1.0024
Industrial wastes | 514.8 | 1
Blast furnace gas | 936 | 1.1021
Coke oven gas | 159.84 | 1.1021
Oxygen steel furnace gas | 655.2 | 1.1021
Oil shale and tar sands | 385.2 | 1
Peat | 381.6 | 1
Values for savings calculation
Power range [kW] | Avg. Power | IE1-IE2 Avg | IE3 | IE4
0.75 - 7.5 | 3.2 | 81.9081 | 86.4562 | 89.08
7.5 - 75 | 34.3 | 91.1733 | 93.2578 | 94.6178
75 - 375 | 201.5 | 94.2506 | 95.6875 | 96.435
375 - 1,000 | 587.5 | 94.535 | 95.94 | 96.62
End-Use | Average VSD Savings [%]
Pumps | 0.28
Fans | 0.28
Air Compressors | 0.12
Cooling compressors | 0.12
Conveyors | 0.12
Other Motors | 0.12
Sector | Operating hours [h/a]
Industry, 1 shift, 5 days/week | 1920
Industry, 2 shifts, 5 days/week | 3840
Industry, 2 shifts, 6 days/week | 4608
Industry, 2 shifts, 7 days/week | 5376
Industry, 3 shifts, 5 days/week | 5760
Industry, 3 shifts, 6 days/week | 6912
Industry, 3 shifts, 7 days/week | 8064
Industry, 3 shift, continuously | 8760
Tertiary Sector | 1480

## National Values (hidden)
Conversion factors
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-]
Electricity
District heat
Natural gas
Gas/Diesel oil
Motor gasoline
Biodiesels
Biogasoline
Other liquid biofuels
Biogas
Wood/wood waste
Other primary solid biomass
Kerosene (other than jet kerosene)
Liquefied petroleum gases
Naphtha
Natural gas liquids
Petroleum coke
Refinery gas
Residual fuel oil
White spirit and SBP
Other petroleum products
Anthracite
Lignite
Charcoal
Coal tar
Coke oven coke and lignite coke
Coking coal
Patent fuel
Sub-bituminous coal
Other bituminous coal
Industrial wastes
Blast furnace gas
Coke oven gas
Oxygen steel furnace gas
Oil shale and tar sands
Peat