## Calculation
Building Automation and Control Systems
This methodology is valid for calculating the impact of installing or upgrading BACS on the energy demand of building(s). It is based on the BAC factor method and can be used for calculating savings in residential and non-residential buildings, for five types of end-use (heating, cooling, domestic hot water, ventilation and lighting) and for the three climate regions. A factor for rebound effects is foreseen.
Data Input
Conversion factors |  |  | EU values for GHG emissions and conversion factors from final to primary energy savings are provided by streamSAVE. If you want to use national values, please fill in the relevant values in the corresponding table in sheet "National values".
Region |  |  | Select climate region: North, West or South. North: Czech Republic, Denmark, Estonia, Finland, Latvia, Lithuania, Poland, Slovakia, Sweden; West: Austria, Belgium, France, Germany, Ireland, Luxemburg, Netherlands; South: Bulgaria, Croatia, Cyprus, Greece, Hungary, Italy, Malta, Portugal, Romania, Slovenia, Spain.
Sector |  |  | Select sector: Residential or Non-residential
Building Type |  |  | Select type of building: Residential: Single Family Home (SFH) or Multiple Family Home (MFH); Non-residential: Offices, Wholesale/Retail, Education, Hospitals/Healthcare, Hotels, Restaurants
End-use Type |  |  | Select type of end-use: Space heating, Cooling, Domestic Hot Water (DHW), Ventilation or Lighting
BAC target |  |  | Select the targeted BAC efficiency class, after improvement, for type of building and type of end-use
Share of energy carriers
| before implementation | share | after implementation | share |  | Parameter explanation
Input energy of appliance before and after implementing the energy saving action. The EU27 averages of energy carriers used in different building types and for different end uses relevant for BACS have been prepared in sheet "EC EU27" and can be included via copy and paste. Shares will be adapted automatically. Please change accordingly when switching between different building- or end-use types.
| total share | 0% | total share | 0% |  | Checksum for total share of energy carriers
| fPE | 0 | fPE | 0 |  | Factor for converting final energy consumption into primary energy consumption
| fGHG | 0 | fGHG | 0 |  | Factor for converting energy consumption into greenhouse gas emissions
| National Data | Unit | Indicative Values | Unit |  | Parameter explanation
BAC before |  | - | Not available | - |  | The average BAC factor for selected region, building type and end-use type
BAC after |  | - | Not available | - |  | The BAC factor corresponding with the selected BAC target for selected building type and end-use type
FECbefore,x |  | kWh/m² useful floor area /a | Not available | kWh/m² useful floor area /a |  | Final Energy Consumption before upgrade of BACS, per sector and end-use type
fBEH |  | - | 1 | - |  | Factor to consider behavioural effects (rebound), value originates from studies on the residential heating & cooling.
cfx |  | - | Not available | - |  | Factor to consider effect of climate zones
A |  | m2 |  | m2 |  | Total useful floor area
Calculation formulas
Article 7 ¦ Total final energy savings (TFES)
Article 3 ¦ Total final energy savings (TFES)
Article 3 ¦ Effect on primary energy consumption (EPEC)
GHG ¦ Greenhouse gas savings (GHGsav)
Calculation results
| National Data | Unit | Indicative Values | Unit |  | Parameter explanation
TFES Article 7 | insufficient data | kWh/a | insufficient data | kWh/a |  | Total final energy savings for Article 7 calculation
TFES Article 3 | insufficient data | kWh/a | insufficient data | kWh/a |  | Total final energy savings for Article 3 calculation
EPEC Article 3 | insufficient data | kWh/a | insufficient data | kWh/a |  | Effect on primary energy consumption for Article 3 calculation
GHGsav | insufficient data | tCO2 | insufficient data | tCO2 |  | Greenhouse gas savings
Costs related to the action
Upgrade to BAC class C
| [euro2020/m2, incl.VAT] | SFH | MFH | Offices | Wholesale/ Retail | Other non-residential | Parameter explanation
| Product cost | 1.5-3.0 | 1.5-3.0 | 9 | 7 | NA | The product cost comprises the purchase of the main components of the BACS system.
| Investment cost, incl. installation cost | 2.8-5.6 | 2.8-5.6 | 21.2 | 16.5 | NA | The investment cost includes both product related costs and the labour cost (i.e. installation and training). The labour costs are reflected in the difference between the investment costs and product costs.
| Maintenance and repair cost | 3% | 3% | 3% | 3% | 3% | The maintenance costs are expressed as a yearly percentage in relation to the required investment costs.
Upgrade to BAC class A
| [euro2020/m2, incl.VAT] | SFH | MFH | Offices | Wholesale /Retail | Other non-residential | Parameter explanation
| Product cost | 4.7-7.1 | 4.3-7.0 | 13.3-14.7 | 12.0-13.2 | NA | The product cost comprises the purchase of the main components of the BACS system.
| Investment cost | 11.1-16.8 | 10.1-16.5 | 31.2-34.6 | 28.2-31.1 | 30 | The investment cost includes both product related costs and the labour cost (i.e. installation and training). The labour costs are reflected in the difference between the investment costs and product costs.
| Maintenance and repair cost | 3% | 3% | 3% | 3% | 3% | The maintenance costs are expressed as a yearly percentage in relation to the required investment costs.

## EU Values (hidden)
Conversion factors
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-] | Remark
Electricity | 133.3 | 2.2813
District heat | 209.9 | 1.6631
Natural gas | 201.96 | 1.007
Gas/Diesel oil | 266.76 | 1.1187
Motor gasoline | 249.48 | 1.1187
Biodiesels | 0 | 1.0008
Biogasoline | 0 | 1.0008
Other liquid biofuels | 0 | 1.0008
Biogas | 0 | 1.0321
Wood/wood waste | 0 | 1.0008
Other primary solid biomass | 0 | 1.0008
Kerosene (other than jet kerosene) | 258.84 | 1.1187
Liquefied petroleum gases | 227.16 | 1.1187
Naphtha | 263.88 | 1.1187
Natural gas liquids | 231.12 | 1.1187
Petroleum coke | 351 | 1.1187
Refinery gas | 207.36 | 1.1187
Residual fuel oil | 278.64 | 1.1187
White spirit and SBP | 263.88 | 1.1187
Other petroleum products | 263.88 | 1.1187
Anthracite | 353.88 | 1.0024
Lignite | 363.6 | 1.0024
Charcoal | 0 | 1.0008
Coal tar | 290.52 | 1.0024
Coke oven coke and lignite coke | 385.2 | 1.0024
Coking coal | 340.56 | 1.0024
Patent fuel | 351 | 1.0024
Sub-bituminous coal | 345.96 | 1.0024
other bituminous coal | 340.56 | 1.0024
Industrial wastes | 514.8 | 1
Blast furnace gas | 936 | 1.1021
Coke oven gas | 159.84 | 1.1021
Oxygen steel furnace gas | 655.2 | 1.1021
Oil shale and tar sands | 385.2 | 1
Solids | 340.56 | 1.0024 |  | Solids = assumed equal to other bituminous coal, as very high share (+/-80%) of solides comprises of other bituminous coal (EU-27, Eurostat, Energy Balances)
Solar | 0 | 1
Geothermal | 0 | 1
Peat | 381.6 | 1
Values for savings calculation
BACbefore
Climate Region | Sector | End-usetype |  | Average BAC
North | SFH | SpaceHeating | NorthSFHSpaceHeating | 1.01
North | SFH | DHW | NorthSFHDHW | 1.109
North | SFH | Cooling | NorthSFHCooling | 1.173
North | SFH | Ventilation | NorthSFHVentilation | 1.091
North | SFH | Lighting | NorthSFHLighting | 1.079
North | MFH | SpaceHeating | NorthMFHSpaceHeating | 1.004
North | MFH | DHW | NorthMFHDHW | 1.109
North | MFH | Cooling | NorthMFHCooling | 1.163
North | MFH | Ventilation | NorthMFHVentilation | 1.084
North | MFH | Lighting | NorthMFHLighting | 1.079
North | Offices | SpaceHeating | NorthOfficesSpaceHeating | 1.195
North | Offices | DHW | NorthOfficesDHW | 1.019
North | Offices | Cooling | NorthOfficesCooling | 1.082
North | Offices | Ventilation | NorthOfficesVentilation | 1.138
North | Offices | Lighting | NorthOfficesLighting | 0.989
North | Wholesale/Retail | SpaceHeating | NorthWholesale/RetailSpaceHeating | 1.139
North | Wholesale/Retail | DHW | NorthWholesale/RetailDHW | 1.092
North | Wholesale/Retail | Cooling | NorthWholesale/RetailCooling | 1.003
North | Wholesale/Retail | Ventilation | NorthWholesale/RetailVentilation | 1.071
North | Wholesale/Retail | Lighting | NorthWholesale/RetailLighting | 0.991
North | Education | SpaceHeating | NorthEducationSpaceHeating | 1.128
North | Education | DHW | NorthEducationDHW | 1.03
North | Education | Cooling | NorthEducationCooling | 0.805
North | Education | Ventilation | NorthEducationVentilation | 0.966
North | Education | Lighting | NorthEducationLighting | 0.991
North | Hospitals/Healthcare | SpaceHeating | NorthHospitals/HealthcareSpaceHeating | 1
North | Hospitals/Healthcare | DHW | NorthHospitals/HealthcareDHW | 0.992
North | Hospitals/Healthcare | Cooling | NorthHospitals/HealthcareCooling | 0.617
North | Hospitals/Healthcare | Ventilation | NorthHospitals/HealthcareVentilation | 1
North | Hospitals/Healthcare | Lighting | NorthHospitals/HealthcareLighting | 1
North | Hotels | SpaceHeating | NorthHotelsSpaceHeating | 1
North | Hotels | DHW | NorthHotelsDHW | 0.992
North | Hotels | Cooling | NorthHotelsCooling | 0.617
North | Hotels | Ventilation | NorthHotelsVentilation | 1
North | Hotels | Lighting | NorthHotelsLighting | 1
North | Restaurants | SpaceHeating | NorthRestaurantsSpaceHeating | 1
North | Restaurants | DHW | NorthRestaurantsDHW | 0.992
North | Restaurants | Cooling | NorthRestaurantsCooling | 0.617
North | Restaurants | Ventilation | NorthRestaurantsVentilation | 1
North | Restaurants | Lighting | NorthRestaurantsLighting | 1
North | Other | SpaceHeating | NorthOtherSpaceHeating | 1.109
North | Other | DHW | NorthOtherDHW | 1.03
North | Other | Cooling | NorthOtherCooling | 1.2
North | Other | Ventilation | NorthOtherVentilation | 1.154
North | Other | Lighting | NorthOtherLighting | 1
West | SFH | SpaceHeating | WestSFHSpaceHeating | 0.991
West | SFH | DHW | WestSFHDHW | 1.109
West | SFH | Cooling | WestSFHCooling | 1.173
West | SFH | Ventilation | WestSFHVentilation | 1.082
West | SFH | Lighting | WestSFHLighting | 1.079
West | MFH | SpaceHeating | WestMFHSpaceHeating | 0.985
West | MFH | DHW | WestMFHDHW | 1.109
West | MFH | Cooling | WestMFHCooling | 1.163
West | MFH | Ventilation | WestMFHVentilation | 1.074
West | MFH | Lighting | WestMFHLighting | 1.079
West | Offices | SpaceHeating | WestOfficesSpaceHeating | 1.189
West | Offices | DHW | WestOfficesDHW | 1.019
West | Offices | Cooling | WestOfficesCooling | 1.082
West | Offices | Ventilation | WestOfficesVentilation | 1.135
West | Offices | Lighting | WestOfficesLighting | 0.989
West | Wholesale/Retail | SpaceHeating | WestWholesale/RetailSpaceHeating | 1.125
West | Wholesale/Retail | DHW | WestWholesale/RetailDHW | 1.092
West | Wholesale/Retail | Cooling | WestWholesale/RetailCooling | 1.003
West | Wholesale/Retail | Ventilation | WestWholesale/RetailVentilation | 1.064
West | Wholesale/Retail | Lighting | WestWholesale/RetailLighting | 0.991
West | Education | SpaceHeating | WestEducationSpaceHeating | 1.128
West | Education | DHW | WestEducationDHW | 1.03
West | Education | Cooling | WestEducationCooling | 0.805
West | Education | Ventilation | WestEducationVentilation | 0.966
West | Education | Lighting | WestEducationLighting | 0.991
West | Hospitals/Healthcare | SpaceHeating | WestHospitals/HealthcareSpaceHeating | 0.978
West | Hospitals/Healthcare | DHW | WestHospitals/HealthcareDHW | 0.992
West | Hospitals/Healthcare | Cooling | WestHospitals/HealthcareCooling | 0.617
West | Hospitals/Healthcare | Ventilation | WestHospitals/HealthcareVentilation | 0.978
West | Hospitals/Healthcare | Lighting | WestHospitals/HealthcareLighting | 1
West | Hotels | SpaceHeating | WestHotelsSpaceHeating | 0.978
West | Hotels | DHW | WestHotelsDHW | 0.992
West | Hotels | Cooling | WestHotelsCooling | 0.617
West | Hotels | Ventilation | WestHotelsVentilation | 0.978
West | Hotels | Lighting | WestHotelsLighting | 1
West | Restaurants | SpaceHeating | WestRestaurantsSpaceHeating | 0.978
West | Restaurants | DHW | WestRestaurantsDHW | 0.992
West | Restaurants | Cooling | WestRestaurantsCooling | 0.617
West | Restaurants | Ventilation | WestRestaurantsVentilation | 0.978
West | Restaurants | Lighting | WestRestaurantsLighting | 1
West | Other | SpaceHeating | WestOtherSpaceHeating | 1.109
West | Other | DHW | WestOtherDHW | 1.03
West | Other | Cooling | WestOtherCooling | 1.2
West | Other | Ventilation | WestOtherVentilation | 1.154
West | Other | Lighting | WestOtherLighting | 1
South | SFH | SpaceHeating | SouthSFHSpaceHeating | 1.028
South | SFH | DHW | SouthSFHDHW | 1.109
South | SFH | Cooling | SouthSFHCooling | 1.173
South | SFH | Ventilation | SouthSFHVentilation | 1.101
South | SFH | Lighting | SouthSFHLighting | 1.079
South | MFH | SpaceHeating | SouthMFHSpaceHeating | 1.022
South | MFH | DHW | SouthMFHDHW | 1.109
South | MFH | Cooling | SouthMFHCooling | 1.163
South | MFH | Ventilation | SouthMFHVentilation | 1.092
South | MFH | Lighting | SouthMFHLighting | 1.079
South | Offices | SpaceHeating | SouthOfficesSpaceHeating | 1.341
South | Offices | DHW | SouthOfficesDHW | 1.036
South | Offices | Cooling | SouthOfficesCooling | 1.205
South | Offices | Ventilation | SouthOfficesVentilation | 1.273
South | Offices | Lighting | SouthOfficesLighting | 0.989
South | Wholesale/Retail | SpaceHeating | SouthWholesale/RetailSpaceHeating | 1.139
South | Wholesale/Retail | DHW | SouthWholesale/RetailDHW | 1.092
South | Wholesale/Retail | Cooling | SouthWholesale/RetailCooling | 1.003
South | Wholesale/Retail | Ventilation | SouthWholesale/RetailVentilation | 1.071
South | Wholesale/Retail | Lighting | SouthWholesale/RetailLighting | 0.991
South | Education | SpaceHeating | SouthEducationSpaceHeating | 1.128
South | Education | DHW | SouthEducationDHW | 1.03
South | Education | Cooling | SouthEducationCooling | 0.816
South | Education | Ventilation | SouthEducationVentilation | 0.972
South | Education | Lighting | SouthEducationLighting | 0.991
South | Hospitals/Healthcare | SpaceHeating | SouthHospitals/HealthcareSpaceHeating | 1.063
South | Hospitals/Healthcare | DHW | SouthHospitals/HealthcareDHW | 1.019
South | Hospitals/Healthcare | Cooling | SouthHospitals/HealthcareCooling | 0.656
South | Hospitals/Healthcare | Ventilation | SouthHospitals/HealthcareVentilation | 1.063
South | Hospitals/Healthcare | Lighting | SouthHospitals/HealthcareLighting | 1
South | Hotels | SpaceHeating | SouthHotelsSpaceHeating | 1.063
South | Hotels | DHW | SouthHotelsDHW | 1.019
South | Hotels | Cooling | SouthHotelsCooling | 0.656
South | Hotels | Ventilation | SouthHotelsVentilation | 1.063
South | Hotels | Lighting | SouthHotelsLighting | 1
South | Restaurants | SpaceHeating | SouthRestaurantsSpaceHeating | 1.063
South | Restaurants | DHW | SouthRestaurantsDHW | 1.019
South | Restaurants | Cooling | SouthRestaurantsCooling | 0.656
South | Restaurants | Ventilation | SouthRestaurantsVentilation | 1.063
South | Restaurants | Lighting | SouthRestaurantsLighting | 1
South | Other | SpaceHeating | SouthOtherSpaceHeating | 1.109
South | Other | DHW | SouthOtherDHW | 1.03
South | Other | Cooling | SouthOtherCooling | 1.2
South | Other | Ventilation | SouthOtherVentilation | 1.154
South | Other | Lighting | SouthOtherLighting | 1
BACafter
Sector | End-use Type | EE class |  | BAC factor
SFH | SpaceHeating | D | SFHSpaceHeatingD | 1.09 |  | for cooling non-residential:
SFH | SpaceHeating | C | SFHSpaceHeatingC | 1 |  | education: factors of lecture halls, cf. MACS
SFH | SpaceHeating | B | SFHSpaceHeatingB | 0.88 |  | hospitals: factors from aggregated thermal
SFH | SpaceHeating | A | SFHSpaceHeatingA | 0.81
MFH | SpaceHeating | D | MFHSpaceHeatingD | 1.09
MFH | SpaceHeating | C | MFHSpaceHeatingC | 1
MFH | SpaceHeating | B | MFHSpaceHeatingB | 0.88
MFH | SpaceHeating | A | MFHSpaceHeatingA | 0.81
Offices | SpaceHeating | D | OfficesSpaceHeatingD | 1.44
Offices | SpaceHeating | C | OfficesSpaceHeatingC | 1
Offices | SpaceHeating | B | OfficesSpaceHeatingB | 0.79
Offices | SpaceHeating | A | OfficesSpaceHeatingA | 0.7
Education | SpaceHeating | D | EducationSpaceHeatingD | 1.2
Education | SpaceHeating | C | EducationSpaceHeatingC | 1
Education | SpaceHeating | B | EducationSpaceHeatingB | 0.88
Education | SpaceHeating | A | EducationSpaceHeatingA | 0.8
Hospitals/Healthcare | SpaceHeating | D | Hospitals/HealthcareSpaceHeatingD | 1.31
Hospitals/Healthcare | SpaceHeating | C | Hospitals/HealthcareSpaceHeatingC | 1
Hospitals/Healthcare | SpaceHeating | B | Hospitals/HealthcareSpaceHeatingB | 0.91
Hospitals/Healthcare | SpaceHeating | A | Hospitals/HealthcareSpaceHeatingA | 0.86
Hotels | SpaceHeating | D | HotelsSpaceHeatingD | 1.17
Hotels | SpaceHeating | C | HotelsSpaceHeatingC | 1
Hotels | SpaceHeating | B | HotelsSpaceHeatingB | 0.85
Hotels | SpaceHeating | A | HotelsSpaceHeatingA | 0.61
Restaurants | SpaceHeating | D | RestaurantsSpaceHeatingD | 1.21
Restaurants | SpaceHeating | C | RestaurantsSpaceHeatingC | 1
Restaurants | SpaceHeating | B | RestaurantsSpaceHeatingB | 0.76
Restaurants | SpaceHeating | A | RestaurantsSpaceHeatingA | 0.69
Wholesale/Retail | SpaceHeating | D | Wholesale/RetailSpaceHeatingD | 1.56
Wholesale/Retail | SpaceHeating | C | Wholesale/RetailSpaceHeatingC | 1
Wholesale/Retail | SpaceHeating | B | Wholesale/RetailSpaceHeatingB | 0.71
Wholesale/Retail | SpaceHeating | A | Wholesale/RetailSpaceHeatingA | 0.46
SFH | Cooling | D | SFHCoolingD | 1.09
SFH | Cooling | C | SFHCoolingC | 1
SFH | Cooling | B | SFHCoolingB | 0.88
SFH | Cooling | A | SFHCoolingA | 0.81
MFH | Cooling | D | MFHCoolingD | 1.09
MFH | Cooling | C | MFHCoolingC | 1
MFH | Cooling | B | MFHCoolingB | 0.88
MFH | Cooling | A | MFHCoolingA | 0.81
Offices | Cooling | D | OfficesCoolingD | 1.57
Offices | Cooling | C | OfficesCoolingC | 1
Offices | Cooling | B | OfficesCoolingB | 0.8
Offices | Cooling | A | OfficesCoolingA | 0.57
Education | Cooling | D | EducationCoolingD | 1.32
Education | Cooling | C | EducationCoolingC | 1
Education | Cooling | B | EducationCoolingB | 0.94
Education | Cooling | A | EducationCoolingA | 0.64
Hospitals/Healthcare | Cooling | D | Hospitals/HealthcareCoolingD | 1.31
Hospitals/Healthcare | Cooling | C | Hospitals/HealthcareCoolingC | 1
Hospitals/Healthcare | Cooling | B | Hospitals/HealthcareCoolingB | 0.91
Hospitals/Healthcare | Cooling | A | Hospitals/HealthcareCoolingA | 0.86
Hotels | Cooling | D | HotelsCoolingD | 1.76
Hotels | Cooling | C | HotelsCoolingC | 1
Hotels | Cooling | B | HotelsCoolingB | 0.79
Hotels | Cooling | A | HotelsCoolingA | 0.76
Restaurants | Cooling | D | RestaurantsCoolingD | 1.39
Restaurants | Cooling | C | RestaurantsCoolingC | 1
Restaurants | Cooling | B | RestaurantsCoolingB | 0.94
Restaurants | Cooling | A | RestaurantsCoolingA | 0.6
Wholesale/Retail | Cooling | D | Wholesale/RetailCoolingD | 1.59
Wholesale/Retail | Cooling | C | Wholesale/RetailCoolingC | 1
Wholesale/Retail | Cooling | B | Wholesale/RetailCoolingB | 0.85
Wholesale/Retail | Cooling | A | Wholesale/RetailCoolingA | 0.55
SFH | DHW | D | SFHDHWD | 1.11
SFH | DHW | C | SFHDHWC | 1
SFH | DHW | B | SFHDHWB | 0.9
SFH | DHW | A | SFHDHWA | 0.8
MFH | DHW | D | MFHDHWD | 1.11
MFH | DHW | C | MFHDHWC | 1
MFH | DHW | B | MFHDHWB | 0.9
MFH | DHW | A | MFHDHWA | 0.8
Offices | DHW | D | OfficesDHWD | 1.11
Offices | DHW | C | OfficesDHWC | 1
Offices | DHW | B | OfficesDHWB | 0.9
Offices | DHW | A | OfficesDHWA | 0.8
Education | DHW | D | EducationDHWD | 1.11
Education | DHW | C | EducationDHWC | 1
Education | DHW | B | EducationDHWB | 0.9
Education | DHW | A | EducationDHWA | 0.8
Hospitals/Healthcare | DHW | D | Hospitals/HealthcareDHWD | 1.11
Hospitals/Healthcare | DHW | C | Hospitals/HealthcareDHWC | 1
Hospitals/Healthcare | DHW | B | Hospitals/HealthcareDHWB | 0.9
Hospitals/Healthcare | DHW | A | Hospitals/HealthcareDHWA | 0.8
Hotels | DHW | D | HotelsDHWD | 1.11
Hotels | DHW | C | HotelsDHWC | 1
Hotels | DHW | B | HotelsDHWB | 0.9
Hotels | DHW | A | HotelsDHWA | 0.8
Restaurants | DHW | D | RestaurantsDHWD | 1.11
Restaurants | DHW | C | RestaurantsDHWC | 1
Restaurants | DHW | B | RestaurantsDHWB | 0.9
Restaurants | DHW | A | RestaurantsDHWA | 0.8
Wholesale/Retail | DHW | D | Wholesale/RetailDHWD | 1.11
Wholesale/Retail | DHW | C | Wholesale/RetailDHWC | 1
Wholesale/Retail | DHW | B | Wholesale/RetailDHWB | 0.9
Wholesale/Retail | DHW | A | Wholesale/RetailDHWA | 0.8
SFH | Ventilation | D | SFHVentilationD | 1.08
SFH | Ventilation | C | SFHVentilationC | 1
SFH | Ventilation | B | SFHVentilationB | 0.93
SFH | Ventilation | A | SFHVentilationA | 0.92
MFH | Ventilation | D | MFHVentilationD | 1.08
MFH | Ventilation | C | MFHVentilationC | 1
MFH | Ventilation | B | MFHVentilationB | 0.93
MFH | Ventilation | A | MFHVentilationA | 0.92
Offices | Ventilation | D | OfficesVentilationD | 1.15
Offices | Ventilation | C | OfficesVentilationC | 1
Offices | Ventilation | B | OfficesVentilationB | 0.86
Offices | Ventilation | A | OfficesVentilationA | 0.72
Education | Ventilation | D | EducationVentilationD | 1.12
Education | Ventilation | C | EducationVentilationC | 1
Education | Ventilation | B | EducationVentilationB | 0.87
Education | Ventilation | A | EducationVentilationA | 0.74
Hospitals/Healthcare | Ventilation | D | Hospitals/HealthcareVentilationD | 1.1
Hospitals/Healthcare | Ventilation | C | Hospitals/HealthcareVentilationC | 1
Hospitals/Healthcare | Ventilation | B | Hospitals/HealthcareVentilationB | 0.98
Hospitals/Healthcare | Ventilation | A | Hospitals/HealthcareVentilationA | 0.96
Hotels | Ventilation | D | HotelsVentilationD | 1.12
Hotels | Ventilation | C | HotelsVentilationC | 1
Hotels | Ventilation | B | HotelsVentilationB | 0.89
Hotels | Ventilation | A | HotelsVentilationA | 0.78
Restaurants | Ventilation | D | RestaurantsVentilationD | 1.09
Restaurants | Ventilation | C | RestaurantsVentilationC | 1
Restaurants | Ventilation | B | RestaurantsVentilationB | 0.96
Restaurants | Ventilation | A | RestaurantsVentilationA | 0.92
Wholesale/Retail | Ventilation | D | Wholesale/RetailVentilationD | 1.13
Wholesale/Retail | Ventilation | C | Wholesale/RetailVentilationC | 1
Wholesale/Retail | Ventilation | B | Wholesale/RetailVentilationB | 0.95
Wholesale/Retail | Ventilation | A | Wholesale/RetailVentilationA | 0.91
SFH | Lighting | D | SFHLightingD | 1.08
SFH | Lighting | C | SFHLightingC | 1
SFH | Lighting | B | SFHLightingB | 0.93
SFH | Lighting | A | SFHLightingA | 0.92
MFH | Lighting | D | MFHLightingD | 1.08
MFH | Lighting | C | MFHLightingC | 1
MFH | Lighting | B | MFHLightingB | 0.93
MFH | Lighting | A | MFHLightingA | 0.92
Offices | Lighting | D | OfficesLightingD | 1.1
Offices | Lighting | C | OfficesLightingC | 1
Offices | Lighting | B | OfficesLightingB | 0.85
Offices | Lighting | A | OfficesLightingA | 0.72
Education | Lighting | D | EducationLightingD | 1.1
Education | Lighting | C | EducationLightingC | 1
Education | Lighting | B | EducationLightingB | 0.88
Education | Lighting | A | EducationLightingA | 0.76
Hospitals/Healthcare | Lighting | D | Hospitals/HealthcareLightingD | 1.2
Hospitals/Healthcare | Lighting | C | Hospitals/HealthcareLightingC | 1
Hospitals/Healthcare | Lighting | B | Hospitals/HealthcareLightingB | 1
Hospitals/Healthcare | Lighting | A | Hospitals/HealthcareLightingA | 1
Hotels | Lighting | D | HotelsLightingD | 1.1
Hotels | Lighting | C | HotelsLightingC | 1
Hotels | Lighting | B | HotelsLightingB | 0.88
Hotels | Lighting | A | HotelsLightingA | 0.76
Restaurants | Lighting | D | RestaurantsLightingD | 1.1
Restaurants | Lighting | C | RestaurantsLightingC | 1
Restaurants | Lighting | B | RestaurantsLightingB | 1
Restaurants | Lighting | A | RestaurantsLightingA | 1
Wholesale/Retail | Lighting | D | Wholesale/RetailLightingD | 1.1
Wholesale/Retail | Lighting | C | Wholesale/RetailLightingC | 1
Wholesale/Retail | Lighting | B | Wholesale/RetailLightingB | 1
Wholesale/Retail | Lighting | A | Wholesale/RetailLightingA | 1
FECbefore,x
Sector | End-use Type |  |  | [kWh/m² useful floor area /a]
Residential | SpaceHeating |  | ResidentialSpaceHeating | 131.9
Residential | Cooling |  | ResidentialCooling | 6.2
Residential | DHW |  | ResidentialDHW | 27.5
Residential | Lighting |  | ResidentialLighting | 3.1
Residential | Ventilation |  | ResidentialVentilation | NA
Non_Residential | SpaceHeating |  | Non_ResidentialSpaceHeating | 130.2
Non_Residential | Cooling |  | Non_ResidentialCooling | 15.1
Non_Residential | DHW |  | Non_ResidentialDHW | 22.1
Non_Residential | Lighting |  | Non_ResidentialLighting | 20.2521
Non_Residential | Ventilation |  | Non_ResidentialVentilation | 15.7
cfx
Climate region | Sector | End-use type |  | Factor
North | Residential | SpaceHeating | NorthResidentialSpaceHeating | 1.21
North | Residential | Cooling | NorthResidentialCooling | 0.64
North | Residential | DHW | NorthResidentialDHW | 1.19
North | Residential | Lighting | NorthResidentialLighting | 0.95
North | Residential | Ventilation | NorthResidentialVentilation | NA
North | Non_Residential | SpaceHeating | NorthNon_ResidentialSpaceHeating | 1.19
North | Non_Residential | Cooling | NorthNon_ResidentialCooling | 0.74
North | Non_Residential | DHW | NorthNon_ResidentialDHW | 0.96
North | Non_Residential | Lighting | NorthNon_ResidentialLighting | 1.048
North | Non_Residential | Ventilation | NorthNon_ResidentialVentilation | 1.1
West | Residential | SpaceHeating | WestResidentialSpaceHeating | 1
West | Residential | Cooling | WestResidentialCooling | 1
West | Residential | DHW | WestResidentialDHW | 1
West | Residential | Lighting | WestResidentialLighting | 1
West | Residential | Ventilation | WestResidentialVentilation | 1
West | Non_Residential | SpaceHeating | WestNon_ResidentialSpaceHeating | 1
West | Non_Residential | Cooling | WestNon_ResidentialCooling | 1
West | Non_Residential | DHW | WestNon_ResidentialDHW | 1
West | Non_Residential | Lighting | WestNon_ResidentialLighting | 1
West | Non_Residential | Ventilation | WestNon_ResidentialVentilation | 1
South | Residential | SpaceHeating | SouthResidentialSpaceHeating | 0.71
South | Residential | Cooling | SouthResidentialCooling | 1.95
South | Residential | DHW | SouthResidentialDHW | 0.97
South | Residential | Lighting | SouthResidentialLighting | 0.92
South | Residential | Ventilation | SouthResidentialVentilation | NA
South | Non_Residential | SpaceHeating | SouthNon_ResidentialSpaceHeating | 0.65
South | Non_Residential | Cooling | SouthNon_ResidentialCooling | 1.45
South | Non_Residential | DHW | SouthNon_ResidentialDHW | 0.98
South | Non_Residential | Lighting | SouthNon_ResidentialLighting | 1.0782
South | Non_Residential | Ventilation | SouthNon_ResidentialVentilation | 1.18
Shareec end-use type
Sector | End-use Type |  |  | % | Remark
Residential | SpaceHeating | Solids | ResidentialSpaceHeatingSolids | 5% | Solids = assumed equal to other bituminous coal, as very high share (+/-80%) of solides comprises of other bituminous coal (EU-27, Eurostat, Energy Balances)
Residential | SpaceHeating | Liquefied petroleum gases | ResidentialSpaceHeatingLiquefied petroleum gases | 1%
Residential | SpaceHeating | Gas/Diesel oil | ResidentialSpaceHeatingGas/Diesel oil | 17%
Residential | SpaceHeating | Natural gas | ResidentialSpaceHeatingNatural gas | 37%
Residential | SpaceHeating | Wood/wood waste | ResidentialSpaceHeatingWood/wood waste | 21%
Residential | SpaceHeating | Geothermal energy | ResidentialSpaceHeatingGeothermal energy | 0%
Residential | SpaceHeating | District heat | ResidentialSpaceHeatingDistrict heat | 12% | Assumed that derived heat = district heat
Residential | SpaceHeating | Electricity | ResidentialSpaceHeatingElectricity | 7%
Non_Residential | SpaceHeating | Solids | Non_ResidentialSpaceHeatingSolids | 2% | Solids = assumed equal to other bituminous coal, as very high share (+/-80%) of solides comprises of other bituminous coal (EU-27, Eurostat, Energy Balances)
Non_Residential | SpaceHeating | Liquefied petroleum gases | Non_ResidentialSpaceHeatingLiquefied petroleum gases | 0%
Non_Residential | SpaceHeating | Gas/Diesel oil | Non_ResidentialSpaceHeatingGas/Diesel oil | 21%
Non_Residential | SpaceHeating | Natural gas | Non_ResidentialSpaceHeatingNatural gas | 46%
Non_Residential | SpaceHeating | Wood/wood waste | Non_ResidentialSpaceHeatingWood/wood waste | 2%
Non_Residential | SpaceHeating | Geothermal energy | Non_ResidentialSpaceHeatingGeothermal energy | 0%
Non_Residential | SpaceHeating | District heat | Non_ResidentialSpaceHeatingDistrict heat | 13% | Assumed that derived heat = district heat
Non_Residential | SpaceHeating | Electricity | Non_ResidentialSpaceHeatingElectricity | 15%
Residential | Cooling | Natural gas | ResidentialCoolingNatural gas | 0.9%
Residential | Cooling | Electricity | ResidentialCoolingElectricity | 99.1%
Non_Residential | Cooling | Natural gas | Non_ResidentialCoolingNatural gas | 0.9%
Non_Residential | Cooling | Electricity | Non_ResidentialCoolingElectricity | 99.1%
Residential | DHW | Solids | ResidentialDHWSolids | 4% | Solids = assumed equal to other bituminous coal, as very high share (+/-80%) of solides comprises of other bituminous coal (EU-27, Eurostat, Energy Balances)
Residential | DHW | Liquefied petroleum gas | ResidentialDHWLiquefied petroleum gas | 6%
Residential | DHW | Gas/Diesel oil | ResidentialDHWGas/Diesel oil | 13%
Residential | DHW | Natural gas | ResidentialDHWNatural gas | 36%
Residential | DHW | Wood/wood waste | ResidentialDHWWood/wood waste | 13%
Residential | DHW | Geothermal energy | ResidentialDHWGeothermal energy | 0%
Residential | DHW | District heat | ResidentialDHWDistrict heat | 9% | Assumed that derived heat = district heat
Residential | DHW | Electricity | ResidentialDHWElectricity | 17%
Residential | DHW | Solar | ResidentialDHWSolar | 3%
Non_Residential | DHW | Solids | Non_ResidentialDHWSolids | 0% | Solids = assumed equal to other bituminous coal, as very high share (+/-80%) of solides comprises of other bituminous coal (EU-27, Eurostat, Energy Balances)
Non_Residential | DHW | Liquefied petroleum gas | Non_ResidentialDHWLiquefied petroleum gas | 3%
Non_Residential | DHW | Gas/Diesel oil | Non_ResidentialDHWGas/Diesel oil | 18%
Non_Residential | DHW | Natural gas | Non_ResidentialDHWNatural gas | 34%
Non_Residential | DHW | Wood/wood waste | Non_ResidentialDHWWood/wood waste | 1%
Non_Residential | DHW | District heat | Non_ResidentialDHWDistrict heat | 9% | Assumed that derived heat = district heat
Non_Residential | DHW | Electricity | Non_ResidentialDHWElectricity | 34%
Non_Residential | DHW | Solar | Non_ResidentialDHWSolar | 1%
Residential | Ventilation | Electricity | ResidentialVentilationElectricity | 100%
Non_Residential | Ventilation | Electricity | Non_ResidentialVentilationElectricity | 100%
Residential | Lighting | Electricity | ResidentialLightingElectricity | 100%
Non_Residential | Lighting | Electricity | Non_ResidentialLightingElectricity | 100%

## EC EU27 (hidden)
EU 27 distribution of energy carriers based on building type and end use
Shareec space heating |  | [dmnl]
Residential | Solids | 5%
| Liquefied petroleum gases | 1%
| Gas/Diesel oil | 17%
| Natural gas | 37%
| Wood/wood waste | 21%
| Geothermal energy | 0%
| District heat | 12%
| Electricity | 7%
Non-Residential (services) | Solids | 2%
| Liquefied petroleum gases | 0%
| Gas/Diesel oil | 21%
| Natural gas | 46%
| Wood/wood waste | 2%
| Geothermal energy | 0%
| District heat | 13%
| Electricity | 15%
Shareec space cooling |  | [dmnl]
| Natural gas | 0.9%
| Electricity | 99.1%
Shareec hot water |  | [dmnl]
Residential | Solids | 4%
| Liquefied petroleum gas | 6%
| Gas/Diesel oil | 13%
| Natural gas | 36%
| Wood/wood waste | 13%
| Geothermal energy | 0%
| District heat | 9%
| Electricity | 17%
| Solar | 3%
Non-Residential (services) | Solids | 0%
| Liquefied petroleum gas | 3%
| Gas/Diesel oil | 18%
| Natural gas | 34%
| Wood/wood waste | 1%
| District heat | 9%
| Electricity | 34%
| Solar | 1%
Shareec ventilation |  | [dmnl]
Residential | Electricity | 100%
Non-residential | Electricity | 100%
Shareec lighting |  | [dmnl]
Residential | Electricity | 100%
Non-residential | Electricity | 100%

## National Values (hidden)
Conversion factors
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-]
Electricity | 0.42 | 2.3
District heat | 0.1 | 0.62
Natural gas | 0.22 | 1.1
Gas/Diesel oil | 0.29 | 1.1
Motor gasoline | 0.29 | 1.1
Biodiesels | 0.04 | 0.2
Biogasoline | 0.04 | 0.2
Other liquid biofuels | 0.04 | 0.2
Biogas | 0.04 | 0.2
Wood/wood waste | 0.04 | 0.2
Other primary solid biomass | 0.04 | 0.2
Kerosene (other than jet kerosene) | 0.29 | 1.1
Liquefied petroleum gases | 0.29 | 1.1
Naphtha
Natural gas liquids | 0.22 | 1.1
Petroleum coke | 0.22 | 1.1
Refinery gas
Residual fuel oil
White spirit and SBP
Other petroleum products | 0.29 | 1.1
Anthracite | 0.36 | 1.2
Lignite | 0.36 | 1.2
Charcoal | 0.36 | 1.2
Coal tar | 0.36 | 1.2
Coke oven coke and lignite coke | 0.36 | 1.2
Coking coal | 0.36 | 1.2
Patent fuel
Sub-bituminous coal | 0.36 | 1.2
Other bituminous coal | 0.36 | 1.2
Industrial wastes
Blast furnace gas
Coke oven gas
Oxygen steel furnace gas
Oil shale and tar sands
Solids
Solar
Geothermal
Peat | 0.36 | 1.1

## Lists (hidden)
Climate Region
North
West
South
Building Type
Non_Residential | Residential
Offices | SFH
Wholesale/Retail | MFH
Education
Hospitals/Healthcare
Hotels
Restaurants
End-use
SpaceHeating
DHW
Cooling
Ventilation
Lighting
BAC classes
A
B
C
D