## Calculation
Cooling Efficiency Improvements in Data Centres
This methodology offers a structured and transparent approach to estimating energy savings from improvements in data centre cooling efficiency. It is based on Power Usage Effectiveness (PUE), an internationally recognized metric that expresses the ratio of a data centre’s total energy consumption to the energy used by its IT equipment. PUE serves as a reliable proxy for evaluating the performance of support systems like cooling, power distribution, and lighting. The core idea is to compare PUE values before and after implementing efficiency measures—such as replacing outdated equipment (e.g., legacy CRAC units), optimizing airflow, or adopting advanced technologies (e.g., free or liquid cooling). A lower PUE indicates reduced non-IT energy overhead.
Data Input
Indicative Values | EU values |  | EU values are provided by streamSAVE+. If you want to use national values, please fill in the relevant values in the corresponding table in sheet "National values".
Category |  |  | Please choose an option for the calculation.
Measure
Share of energy carriers
| before implementation | share | after implementation | share | Parameter explanation
|  | 0% |  | 0% | input energy of appliance before and after implementing the energy saving action
|  | 0% |  | 0% | input energy of appliance before and after implementing the energy saving action
|  | 0% |  | 0% | input energy of appliance before and after implementing the energy saving action
|  | 0% |  | 0% | input energy of appliance before and after implementing the energy saving action
|  | 0% |  | 0% | input energy of appliance before and after implementing the energy saving action
| total share | 0% | total share | 0% | checksum for total share of energy carriers
| fPE, before | 0 | fPE, after | 0 | Factor for converting final energy consumption into primary energy consumption
| fGHG, before | 0 | fGHG, after | 0 | Factor for converting energy consumption into greenhouse gas emissions
| national values | Unit | indicative calculation values | Unit | Parameter explanation
ECbefore |  | kWh/a | 0 | kWh/a | Annual energy consumption of ICT equipment (servers, storage, networking) [kWh/year]
PUEbefore |  | - | 0 | - | Power Usage Effectiveness before implementation of the action [without unit]
PUEafter |  | - | 0 | - | Power Usage Effectiveness after implementation of the action [without unit]
Scooling |  | % | 0% | % | Estimated or measured share of cooling within the non-ICT loads (cooling, UPS, lighting)
Calculation formulas
Article 8 ¦ Total final energy savings (TFES)
Article 4 ¦ Total final energy savings (TFES)
Article 4 ¦ Total primary energy savings (TPES)
GHG ¦ Greenhouse gas savings (GHGsav)
Calculation results
| national values | Unit | indicative calculation values | Unit | Parameter explanation
TFES Article 8 | 0 | kWh/a | 0 | kWh/a | Total final energy savings for Article 8 calculation
TFES Article 4 | 0 | kWh/a | 0 | kWh/a | Total final energy savings for Article 4 calculation
TPES Article 4 | 0 | kWh/a | 0 | kWh/a | Total primary energy savings for Article 4 calculation
GHGsav | 0 | tCO2e | 0 | tCO2e | Greenhouse gas savings (CO2 equivalents)
Costs related to the action
| [a] |  | LifetimePA [years] |  | Parameter explanation
| Upgrade CRAC/CRAH units to variable-speed systems |  | 15 |  | Lifetime for each efficiency measure
| Transition to chilled water system with air-side economizers |  | 15 |  | Lifetime for each efficiency measure
| Implement free cooling (air-side, water-side, TES etc.) |  | 15 |  | Lifetime for each efficiency measure
| Deploy liquid cooling (direct-to-chip or immersion) |  | 15 |  | Lifetime for each efficiency measure
| Optimize two-phase/passive cooling (e.g., thermosiphon loops) |  | 15 |  | Lifetime for each efficiency measure
| Integrate thermal energy storage (TES) for peak shaving and free cooling |  | 15 |  | Lifetime for each efficiency measure
| Technology |  | Total CapEx per Watt [euro2024/a]
| Air-Cooled (10 kW/rack) |  | 6.46 |  | Investment costs for baseline Air Cooled 10 kW/rack data center
| Liquid-Cooled (10 kW/rack) |  | 6.42 |  | Investment costs for cooling efficiency improvements 10 kW/rack data center
| Liquid-Cooled (20 kW/rack) |  | 5.83 |  | Investment costs for cooling efficiency improvements 20 kW/rack data center
| Liquid-Cooled (40 kW/rack) |  | 5.54 |  | Investment costs for cooling efficiency improvements 40 kW/rack data center

## EU Values
Conversion factors | [values based on Eurostat energy balances of 2023]
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-]
Electricity | 104.39 | 2.064
District heat | 194.7 | 1.592
Natural gas | 201.96 | 1.007
Gas/Diesel oil | 266.76 | 1.117
Motor gasoline | 249.48 | 1.117
Biodiesels | 0 | 1.002
Biogasoline | 0 | 1.002
Other liquid biofuels | 0 | 1.002
Biogas | 0 | 1.026
Wood/wood waste | 0 | 1.002
Other primary solid biomass | 0 | 1.002
Kerosene (other than jet kerosene) | 258.84 | 1.117
Liquefied petroleum gases | 227.16 | 1.117
Naphtha | 263.88 | 1.117
Natural gas liquids | 231.12 | 1.117
Petroleum coke | 351 | 1.117
Refinery gas | 207.36 | 1.117
Residual fuel oil | 278.64 | 1.117
White spirit and SBP | 263.88 | 1.117
Other petroleum products | 263.88 | 1.117
Anthracite | 353.88 | 1.002
Lignite | 363.6 | 1.002
Charcoal | 0 | 1.002
Coal tar | 290.52 | 1.002
Coke oven coke and lignite coke | 385.2 | 1.002
Coking coal | 340.56 | 1.002
Patent fuel | 351 | 1.002
Sub-bituminous coal | 345.96 | 1.002
Other bituminous coal | 340.56 | 1.002
Industrial wastes | 514.8 | 1
Blast furnace gas | 936 | 1.089
Coke oven gas | 159.84 | 1.089
Oxygen steel furnace gas | 655.2 | 1.089
Oil shale and tar sands | 385.2 | 1
Peat | 381.6 | 1.002
Values for savings calculation
Category | IT Power | [kWh/a] | Scooling
Very Small (100–500 kW) | 100–500 kW | 1530000 | 77.5%
Small (500–1,000 kW) | 500–1,000 kW | 3800000 | 67.5%
Medium (1–2 MW) | 1–2 MW | 8500000 | 52.5%
Large (2–10 MW) | 2–10 MW | 37150000 | 46%
Very Large (>10 MW) | >10 MW | 65000000 | 36%
Measure | Baseline PUE | Improved PUE
Upgrade CRAC/CRAH units to variable-speed systems | 1.8 | 1.55
Transition to chilled water system with air-side economizers | 1.6 | 1.4
Implement free cooling (air-side, water-side, TES etc.) | 1.7 | 1.3
Deploy liquid cooling (direct-to-chip or immersion) | 1.7 | 1.06
Optimize two-phase/passive cooling (e.g., thermosiphon loops) | 1.625 | 1.2
Integrate thermal energy storage (TES) for peak shaving and free cooling | 1.7 | 1.3

## National Values
Conversion factors
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-]
Electricity | 150 | 2
District heat
Natural gas
Gas/Diesel oil
Motor gasoline
Biodiesels
Biogasoline
Other liquid biofuels
Biogas
Wood/wood waste
Other primary solid biomass
Kerosene (other than jet kerosene)
Liquefied petroleum gases
Naphtha
Natural gas liquids
Petroleum coke
Refinery gas
Residual fuel oil
White spirit and SBP
Other petroleum products
Anthracite
Lignite
Charcoal
Coal tar
Coke oven coke and lignite coke
Coking coal
Patent fuel
Sub-bituminous coal
Other bituminous coal
Industrial wastes
Blast furnace gas
Coke oven gas
Oxygen steel furnace gas
Oil shale and tar sands
Peat