## Calculation
Heat recovery in ventilation units
[LONG DESCRIPTION] This methodology can be used for calculating the impact of installing or upgrading heat recovery in ventilation units on the energy demand of buildings. It can be applied to a residential or non-residential building, retrofitted as well as non-retrofitted in any of the EU27 countries. The methodology is based on an analysis of several existing methodologies documented in literature and methodologies already in use in countries Czech Republic, France, Hungary, Latvia, Lithuania, Luxemburg and Slovenia. Via the use of a heat recovery system, part of the energy incorporated in the exhaust air is recovered and used to reduce the energy demand required for heating the supply air. Only the efficiency in relation to the heat recovery system is taken into account. This is done via the thermal efficiency of the heat recovery system hHR,after - determined according to (EU) 1253/2014 - which is compared to a situation before without heat recovery or in case of an existing ventilation system with heat recovery that is being replaced or upgraded, to the thermal efficiency of the heat recovery system already present. An estimate for the factor for correction of behavioural effects in case of non-residential buildings is not available, but currently set to 1,00 to enable calculation. It is recommended to implement such factor. It is to be estimated for the national context. For all other input parameters, indicative values are available in the methodology. In case only for part of the parameters national values are available; in Data Input, use the National values calculation type (field Indicative Values), also include relevant input in the fields 'Region', 'Building type' and 'Technology type' and, i) use national values for the share of energy carriers for space heating shareec or copypaste the indicative values from the sheet 'EC EU27' for the respective building type in case no national values are available. ii) copy the indicative values shown in the column 'indicative calculation values' for those parameters for which no national values are available into the column 'national values'. National specific data is preferred, if available.
Data Input
Indicative Values |  |  | EU values are provided by streamSAVE. If you want to use national values, please fill in the relevant values in the corresponding table in sheet "National values".
Region |  |  | Indicative values are available for different climatic regions. Please select climate region: North, West or South. North: Czech Republic, Denmark, Estonia, Finland, Latvia, Lithuania, Poland, Slovakia, Sweden; West: Austria, Belgium, France, Germany, Ireland, Luxemburg, Netherlands; South: Bulgaria, Croatia, Cyprus, Greece, Hungary, Italy, Malta, Portugal, Romania, Slovenia, Spain. This field only applies in case the EU Values calculation type is selected in the field Indicative Values.
Building type |  |  | Indicative values are available for different building types. Please choose an option for the calculation.
Technology type |  |  | Indicative values are available for different technology types. Please choose an option for the calculation.
Share of energy carriers
| before implementation | share | after implementation | share | Parameter explanation
|  | 0% |  | 0% | Select energy carriers and share of energy carriers in the final energy use for space heating before and after implementing the energy saving action. In case no information is available for the national energy carrier mix of the heating system - but there is national data for the conversion factors available, values for the energy mix can be copied from sheet EC EU 27 which represent the average energ carrier mix for space heating in EU27. Please copy ranges accordingly when switching between different building types.
| total share | 0% | total share | 0% | checksum for total share of energy carriers
| fPE, before | 0 | fPE, after | 0 | Factor for converting final energy consumption into primary energy consumption for space heating
| fGHG, before | 0 | fGHG, after | 0 | Factor for converting energy consumption into greenhouse gas emissions for space heating
| national values | Unit | indicative calculation values | Unit | Parameter explanation
hHR,before |  | - | Not available | - | Thermal efficiency of the heat recovery system before the implemented action
hHR,after |  | - | Not available | - | Thermal efficiency of the implemented heat recovery system
A |  | m² | Not available | m² | Useful floor area of the zone serviced by the ventilation system
h |  | m | Not available | m | Average height of the zone serviced by the ventilation system
ACH |  | m³/h/m³ | Not available | m³/h/m³ | Hourly air change rate
DT |  | °C | Not available | °C | Average temperature difference between indoor and outdoor environment during the heating season
tSH |  | h | Not available | h | Length of the heating season
hSH |  | - | Not available | - | Thermal efficiency of the space heating system
fBEH |  | - | Not available | - | Factor to consider behavioural effects
Calculation formulas
Article 8 ¦ Total final energy savings (TFES)
Article 4 ¦ Total final energy savings (TFES)
Article 4 ¦ Total primary energy savings (TPES)
GHG ¦ Greenhouse gas savings (GHGsav)
Calculation resuls
| project specific values | Unit | indicative calculation values | Unit | Parameter explanation
TFES Article 8 | insufficient data | kWh/a | insufficient data | kWh/a | Total final energy savings for Article 8 calculation
TFES Article 4 | insufficient data | kWh/a | insufficient data | kWh/a | Total final energy savings for Article 4 calculation
TPES Article 4 | insufficient data | kWh/a | insufficient data | kWh/a | Total primary energy savings for Article 4 calculation
GHGsav | insufficient data | tCO2e | insufficient data | tCO2e | Greenhouse gas savings (CO2 equivalents)
Costs related to the action
Costs excl. VAT
| Investment costs |  | [Euro2024/unit] |  | Parameter explanation
| Residential |  | CBVU New built | 4.915 | Investment expenditures include the purchase, delivery and installation of the products. The purchase cost is based on the street price, meaning that the values include margins for wholesale and retail on top of the manufacturer selling price. Installation costs include installation materials and labour costs.
|  |  | CBVU Renovation | 6.35
|  |  | CBVU Replacement | n.a.
|  |  | LBVU New built | 1.415
|  |  | LBVU Renovation | 1.415
|  |  | LBVU Replacement | n.a.
| Non-residential |  | CBVU/CHRV New built | 30.063
|  |  | CBVU/CHRV Renovation | 33.045
|  |  | CBVU/CHRV Replacement | 8.408
| Variable operational costs |  | [Euro2024/year]
| Costs of reduced fuel input |  | Fuel prices before/after from Eurostat |  | Variable operational expenditures consist of energy costs of the space heating system.
| Fixed operational costs |  | [Euro2024/unit/year]
| Residential |  | CBVU | 67 | Fixed operational expenditures are related to the maintenance of the ventilation system with heat recovery. Maintenance expenditures include costs for e.g. filter replacement, cleaning of fans, ducts, valves and grills, and small repairs.
|  |  | LBVU | 29
| Non-residential |  | CBVU/CHRV | 175
| Lifetime |  | [a]
| Technical lifetime |  |  | 15 | Estimate for the technical lifetime expectancy of heat recovery systems and of ventilation systems with heat recovery, valid for residential and non-residential buildings.
Legend |  |  | CBVU |  | Central Bidirectional Ventilation Unit
|  |  | LBVU |  | Local Bidirectional Ventilation Unit
|  |  | CHRV |  | Central Heat Recovery Ventilation

## EU Values
Conversion factors | [values based on Eurostat energy balances of 2023]
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-] | Remark
Reference heating system - residential | 155.5973 | 1.1677
Reference heating system - non-residential | 180.7236 | 1.3097
Electricity | 104.39 | 2.064
District heat | 194.7 | 1.592
Natural gas | 201.96 | 1.007
Gas/Diesel oil | 266.76 | 1.117
Motor gasoline | 249.48 | 1.117
Biodiesels | 0 | 1.002
Biogasoline | 0 | 1.002
Other liquid biofuels | 0 | 1.002
Biogas | 0 | 1.026
Wood/wood waste | 0 | 1.002
Other primary solid biomass | 0 | 1.002
Kerosene (other than jet kerosene) | 258.84 | 1.117
Liquefied petroleum gases | 227.16 | 1.117
Naphtha | 263.88 | 1.117
Natural gas liquids | 231.12 | 1.117
Petroleum coke | 351 | 1.117
Refinery gas | 207.36 | 1.117
Residual fuel oil | 278.64 | 1.117
White spirit and SBP | 263.88 | 1.117
Other petroleum products | 263.88 | 1.117
Anthracite | 353.88 | 1.002
Lignite | 363.6 | 1.002
Charcoal | 0 | 1.002
Coal tar | 290.52 | 1.002
Coke oven coke and lignite coke | 385.2 | 1.002
Coking coal | 340.56 | 1.002
Patent fuel | 351 | 1.002
Sub-bituminous coal | 345.96 | 1.002
Other bituminous coal | 340.56 | 1.002
Industrial wastes | 514.8 | 1
Blast furnace gas | 936 | 1.089
Coke oven gas | 159.84 | 1.089
Oxygen steel furnace gas | 655.2 | 1.089
Oil shale and tar sands | 385.2 | 1
Solids | 340.56 | 1.002 | Solids = assumed equal to other bituminous coal, as very high share of solides comprises of other bituminous coal (EU-27, Eurostat, Energy Balances)
Solar | 0 | 1
Geothermal | 0 | 1
Peat | 381.6 | 1.002
Values for savings calculation
hHR,after | [-]
Technology_type | Eta_HR_after
Run-around heat recovery system | 0.68
All other types of heat recovery system | 0.73
hHR,before | [-]
Building_type | Eta_HR_before
Residential | 0.044
Non-residential | 0.381
A | [m²]
Building_type | A
Residential | 95.079
Non-residential | 900
h | [m]
Building_type | h
Residential | 2.9
Non-residential | 4
ACH | [-]
Building_type | ACH
Residential | 0.3
Non-residential | 0.39
rair | [kg/m³]
density of air | 1.293
cp,air | [kWh/(kg.K)]
specific heat of air | 0.000279
DT | [°C]
Climate_region | D_T
North | 14.5
West | 9.5
South | 5
tSH | [h]
Climate_region | t_SH
North | 6552
West | 5112
South | 4392
hSH | [-]
Building_type | Eta_SH
Residential | 0.75
Non-residential | 0.75
fBEH | [-]
Building_type | f_BEH
Residential | 0.8
Non-residential | 1 | fBEH is not available for non-residential buildings - currently set equal to 1 to enable calculation
Lifetime of savings | [a]
Lifetime of savings | 15

## EC EU27
EU 27 distribution of energy carriers based on building type for space heating
Building_type | Energy_carrier_SH |  | Shareec Space heating [%] | Remark
Residential | Solids | ResidentialSolids | 3.52% | Solids = assumed equal to other bituminous coal, as very high share of solides comprises of other bituminous coal (EU-27, Eurostat, Energy Balances)
Residential | Liquefied petroleum gases | ResidentialLiquefied petroleum gases | 1.48%
Residential | Gas/Diesel oil | ResidentialGas/Diesel oil | 9.91%
Residential | Natural gas | ResidentialNatural gas | 41.3%
Residential | Wood/wood waste | ResidentialWood/wood waste | 24.49%
Residential | Geothermal energy | ResidentialGeothermal energy | 0.03%
Residential | District heat | ResidentialDistrict heat | 11.39% | Assumed that derived heat = district heat
Residential | Electricity | ResidentialElectricity | 7.88%
Non-residential | Solids | Non-residentialSolids | 1.24%
Non-residential | Liquefied petroleum gases | Non-residentialLiquefied petroleum gases | 0.36%
Non-residential | Gas/Diesel oil | Non-residentialGas/Diesel oil | 14.5%
Non-residential | Natural gas | Non-residentialNatural gas | 43.93%
Non-residential | Wood/wood waste | Non-residentialWood/wood waste | 5.7%
Non-residential | Geothermal energy | Non-residentialGeothermal energy | 0.4%
Non-residential | District heat | Non-residentialDistrict heat | 14.3%
Non-residential | Electricity | Non-residentialElectricity | 19.58%

## National Values
Conversion factors
Energy Carrier | emission factor [gCO2/kWh] | factor final to primary [-] | Parameter explanation
Reference heating system - residential |  |  | In case no national values are available, EU27 average conversion factors per energy carrier have been prepared in sheet 'EU values' and can be included via copy and paste.
Reference heating system - non-residential
Electricity
District heat
Natural gas
Gas/Diesel oil
Motor gasoline
Biodiesels
Biogasoline
Other liquid biofuels
Biogas
Wood/wood waste
Other primary solid biomass
Kerosene (other than jet kerosene)
Liquefied petroleum gases
Naphtha
Natural gas liquids
Petroleum coke
Refinery gas
Residual fuel oil
White spirit and SBP
Other petroleum products
Anthracite
Lignite
Charcoal
Coal tar
Coke oven coke and lignite coke
Coking coal
Patent fuel
Sub-bituminous coal
Other bituminous coal
Industrial wastes
Blast furnace gas
Coke oven gas
Oxygen steel furnace gas
Oil shale and tar sands
Solids
Solar
Geothermal
Peat

## Lists
Calculation_type
National values
EU values
Climate_region
North
West
South
Building_type
Residential
Non-residential
Technology_type
Run-around heat recovery system
All other types of heat recovery system